## Slide 1: Data-Driven Real-Time State Estimator Using Machine Learning for Transmission System
Evangelos Farantatos, Paul Myrda, Mahendra Patel
EPRI
Anamitra Pal, Assistant Professor
Arizona State University
Feb 23, 2022
Tasks 5 and 6 Update

## Slide 2: Presentation Outline
Project Objectives
Project Timeline
Task 2 Summary
Task 3 Summary
Task 5: Output Post-processing
  Handling bad data and missing data
  Differentiating bad data and extreme data
Task 6: Software Development
  GUI visualization
Summary and Upcoming Tasks

## Slide 3
Data Driven Real Time State Estimator using Machine Learning for Transmission Systems
OBJECTIVES:
Develop a Bayesian state estimator with the following characteristics:
Capable of estimating states (complex voltages) in the presence of measurements from topologically unobserved systems
Independent of the measurement error distribution
Capable of estimating states at the rate of 30 samples per second utilizing time-synchronized measurements as real-time inputs
Develop approaches to counter bad data and test their robustness against different types of bad/missing data
Develop ways to update the Machine Learning (ML)-based state estimator in presence of topology changes and system events
Approximating conditional expectation
Probability distribution fitting from input data
Monte Carlo sampling
Training sample generation
Deep neural network (DNN) training
Optimized DNN parameters
Real-time PMU measurements
State Estimates
Offline Learning
Online Implementation

## Slide 4
Data Driven Real Time State Estimator using Machine Learning for Transmission Systems
Task | Topic | Due Date | Oct.-Feb. | Mar.-Jul. | Aug.-Nov.
1 | Machine Learning Model Development for State Estimation | Feb. 28, 2021 |  |  | 
2 | Machine Learning Based State Estimation with Limited Number of PMUs | Jul. 30, 2021 |  |  | 
3 | Machine Learning Based State Estimation with Missing and Bad Data | Nov. 30, 2021 |  |  | 
4 | Machine Learning Based State Estimation under Event Conditions and System Topology Changes | Nov. 30, 2021 |  |  | 
Timeline

## Slide 5
Task | Topic | Due Date | Dec.-Apr. | May-Sep. | Oct.-Dec.
5 | Machine Learning Based State Estimation Output Post-Processing | April 30, 2022 |  |  | 
6 | Machine Learning Based State Estimation Software Development | Sep. 30, 2022 |  |  | 
7 | Machine Learning Based State Estimation Case Studies | Dec. 31, 2022 |  |  | 
-- | Final Report and Software Tool | Dec. 31, 2022 |  |  | 
Timeline Contd.
Data Driven Real Time State Estimator using Machine Learning for Transmission Systems

## Slide 6: Summary of Tasks 2 and 3

## Slide 7: Task 2 Summary: ML-based State Estimator
Optimal tuning of the hyperparameters of a deep neural network (DNN) was carried out using a random search framework
Even with smaller number of PMUs [13 instead of 32], the DNN state estimation (SE) model was able to reasonably estimate the states of the system
The state estimation results were good even in presence of non-Gaussian noise in the measurements

## Slide 8: DNN-SE Results with 13 PMUs in presence of Laplacian noise
Red color: Bus locations where PMUs are placed
Blue color: Bus locations where PMUs are not placed

## Slide 9: Task 3 Summary: Bad Data and Missing Data Detection
Normalized Input Data
Bad Data
Bad data is identified using Wald Test
Two hypotheses are tested:
  𝐻0 models the measurement without bad data
  𝐻1 models the measurement with bad data
𝐻0 has a Gaussian distribution with mean 𝜇 and variance 𝜎2, both of which are learned during DNN training
During testing with bad data, 𝐻1 has a Gaussian distribution that has mean and variance different from 𝐻0
Bad data is detected when the deviation exceeds a certain threshold
Mathematically, the Wald test is given by:
is the false positive alarm percentage and is usually set to 5%

## Slide 10: Bad Data and Missing Data Replacement by Mean value
Obtain 𝜇 and 𝜎2 from normalized training data
Set the threshold for false positive
Normalized real-time data points larger than the threshold will be replaced by the expected value of the normal distribution

## Slide 11: Task 5: Machine Learning Based State Estimation Output Post-Processing

## Slide 12: Bad Data and Missing Data Replacement by Nearest Operating Condition (OC)
Obtain 𝜇 and 𝜎2 from normalized training data
Set the threshold for false positive
Normalized real-time data points larger than the threshold will be replaced by the corresponding value from the closest OC in the L2 sense

## Slide 13: Bad Data Detection with and without Replacement
If bad data is not replaced, the voltage magnitude MAE increases from 0.0049 to 0.1546 when the probability of bad data is increased from 0 to 0.5
Replacing bad data using either of the two approaches resulted in much higher accuracy

## Slide 14: Bad Data Detection with and without Replacement
A similar effect was observed for voltage phase angle estimation
In presence of 50% bad data, the voltage angle MAE went up to 4.63°
For the same case, when the bad data was replaced using mean and nearest OC, the MAE decreased to 0.69° and 0.61°, respectively

## Slide 15: Improvement in Bad Data Replacement Method
Originally, the bad data was replaced using the mean value (in Task 3)
A better method is to replace the bad data with the data from the nearest OC calculated in the L2 norm sense using the remaining good data

## Slide 16: Improvement in Bad Data Replacement Method
More pronounced difference was observed in voltage phase angle (than voltage magnitude) by using the improved bad data replacement method

## Slide 17: Missing Data Replacement
Similarly, in case of missing data also, the method of replacing using the data from nearest OC can be seen to be more advantageous than simply replacing it with mean of the same feature

## Slide 18: Extreme Scenario vs. Bad Data
It may so happen that the Wald test might classify the extreme scenarios occurring in the power system as bad data
A filter is designed based on power system domain knowledge to overcome this drawback
Filter: If a data point is identified as bad by the Wald test for different PMUs which are within hops of each other (where ), the data corresponds to an extreme operating condition and should not be treated as a bad data
For such data points, the results of the Wald Test are suppressed

## Slide 19: Extreme Scenario Generation - Example
Red color denotes the buses with PMU
An OC was identified such that the current and voltage variables in the Blue oval of the network have extreme values
For this OC, the line flows in branches 8-9 and 10-9 increased sharply

## Slide 20: Extreme Scenario (ES) Detection Filter - Results
Variables detected to be crossing the Wald Test threshold in this case are:
Vm – Bus 9
Va – Bus 8, Bus 9
Im – Line 8-9, 9-10
Ia – Line 9-10
The proposed filter recognizes this as an extreme scenario
The results with and without use of this extreme scenario filter are displayed

## Slide 21: Differentiating Extreme Scenario From Bad Data
For the same extreme scenario discussed on the previous slide, bad data was added to the voltage magnitude and phase angle measurements of PMUs placed at buses 81 and 87
The ES filter identified these two data as bad data and replaced them
However, the measurements corresponding to the extreme scenario (i.e., the PMUs placed at buses 8, 9, and 10) were not altered

## Slide 22: Task 6: Machine Learning Based State Estimation Software Development

## Slide 23: Draft Interface

## Slide 24
Possible Interactions
Filter bar - this will help users filter nodes of a certain voltage magnitude, error, and angle
Zooming and Panning - If number of nodes and edges increase, users can zoom to a certain region and pan across the graph
https://bl.ocks.org/EfratVil/92f894ac0ba265192411e73f633a3e2f
Lasso Selection - If number of nodes and edges increase, users can zoom to a certain region and pan across the graph
https://bl.ocks.org/skokenes/a85800be6d89c76c1ca98493ae777572
Tooltips - This will help users to get more information about the hovered node

## Slide 25: Conclusion & Upcoming Tasks
A better method to replace bad data was identified and implemented
An intelligent alarming technique to differentiate between bad data and extreme scenarios was developed
Next Tasks:
  Detecting events/network parameters (breaker opening, tracking line impedances)
  Implementing the presented interface

## Slide 26: Q&A Thank You For Your Time